## 1 Background Noise by persons
Number of (active) persons → | 25 | Background Noise Level Calculation Tool, Version 1.1 Persons
Room Volume [m³] → | 1000
Octave Band values | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz
RT60 [s] → | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sound Power Levels LW [dB ] (*1) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
normal speech (*1) | 55 | 65.3 | 69 | 63 | 55.8 | 49.8 | 44.5 | 71.5 | 68.4
raised speech (*1) | 60 | 69.5 | 74.9 | 71.9 | 63.8 | 57.3 | 48.4 | 77.7 | 75.5
loud speech (*1) | 64 | 72.1 | 79.6 | 80.2 | 72.9 | 65.9 | 54.8 | 83.8 | 82.6
shouted speech (*1) | 65 | 73.1 | 84 | 89.3 | 82.4 | 74.9 | 64.1 | 91.2 | 90.9
loud speech (*2) | 63.1 | 79.6422 | 80.6634 | 77.4312 | 72.4133 | 68.4088 | 63.5732 | 84.7 | 82
Noise-Level Results Ln in dB SPL (*3,4) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
normal speech (*1) | 52.9317 | 63.2317 | 66.9317 | 60.9317 | 53.7317 | 47.7317 | 42.4317 | 69.4384 | 66.3303
Angehobenes Sprechen | 1.9641e-07 | 2.1046e-06 | 4.9337e-06 | 1.2393e-06 | 2.3614e-07 | 5.9316e-08 | 1.7505e-08
Lautes Sprechen | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 8.787e-06
Schreien | 36.8317 | 54.6317 | 63.7317 | 60.9317 | 54.9317 | 48.7317 | 41.3317
Sum of 10*Antilog | 4.8214e-09 | 2.9052e-07 | 2.3614e-06 | 1.2393e-06 | 3.113e-07 | 7.4675e-08 | 1.3589e-08 | 4.2956e-06
raused speech (*1) | 57.9317 | 67.4317 | 72.8317 | 69.8317 | 61.7317 | 55.2317 | 46.3317 | 75.6629 | 73.425
| 6.2112e-07 | 5.5357e-06 | 1.9194e-05 | 9.62e-06 | 1.49e-06 | 3.3356e-07 | 4.2971e-08
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 3.6838e-05
| 41.8317 | 58.8317 | 69.6317 | 69.8317 | 62.9317 | 56.2317 | 45.2317
| 1.5247e-08 | 7.6414e-07 | 9.187e-06 | 9.62e-06 | 1.9641e-06 | 4.1993e-07 | 3.3356e-08 | 2.2004e-05
loud speech (*1) | 61.9317 | 70.0317 | 77.5317 | 78.1317 | 70.8317 | 63.8317 | 52.7317 | 81.7036 | 80.5205
| 1.5602e-06 | 1.0073e-05 | 5.6647e-05 | 6.5039e-05 | 1.2111e-05 | 2.4164e-06 | 1.8757e-07
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.00014803
| 45.8317 | 61.4317 | 74.3317 | 78.1317 | 72.0317 | 64.8317 | 51.6317
| 3.8298e-08 | 1.3905e-06 | 2.7113e-05 | 6.5039e-05 | 1.5965e-05 | 3.0421e-06 | 1.456e-07 | 0.00011273
shouted speech (*1) | 62.9317 | 71.0317 | 81.9317 | 87.2317 | 80.3317 | 72.8317 | 62.0317 | 89.1806 | 88.8808
| 1.9641e-06 | 1.2682e-05 | 0.00015602 | 0.00052866 | 0.00010794 | 1.9194e-05 | 1.5965e-06
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.00082805
| 46.8317 | 62.4317 | 78.7317 | 87.2317 | 81.5317 | 73.8317 | 60.9317
| 4.8214e-08 | 1.7505e-06 | 7.4675e-05 | 0.00052866 | 0.00014229 | 2.4164e-05 | 1.2393e-06 | 0.00077282
loud speech (*2) | 61.0317 | 77.5739 | 78.5951 | 75.363 | 70.345 | 66.3405 | 61.505 | 82.5949 | 79.9004
| 1.2682e-06 | 5.72e-05 | 7.2362e-05 | 3.4379e-05 | 1.0827e-05 | 4.3058e-06 | 1.4142e-06
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.00018176
| 44.9317 | 68.9739 | 75.3951 | 75.363 | 71.545 | 67.3405 | 60.405
| 3.113e-08 | 7.8958e-06 | 3.4635e-05 | 3.4379e-05 | 1.4273e-05 | 5.4206e-06 | 1.0977e-06 | 9.7732e-05
Remarks: | The example is for 25 people talking in a medium sized room (1.000m³) with RT60 according to DIN 18041 (A2 Speech). Are all people talking? At which level are they talking? Is there any machninery that is producing sigificant noise during voice alarm?
Two different approaches are used for noise level calculation: *1 Sound Power Levels referenced to Lw = 0 dB for 10 -12 W are taken from: a ) ANSI 3.5-1997. Methods for Calculation of the Speech Intelligibility Index. American National Standard. New York (Reaffirmed in 2007). b) J.H. Rindel, C.L. Christensen, A.C. Gade: Dynamic sound source for simulating the Lombard effect in room acoustic modeling software. Proceedings of Internoise 2012, New York, 2012. *2 Equivalent sound power level ("loud speech") according to VDI 3770; composition of the spectral sound power levels corresponds half to a male and half to a female person according to EN 60268-16 (2011) *2 Output result is Sound Pressure Level referenced to L = 0 dB for 20 -6 Pa ¦ Noise-Level Results Ln in dB SPL are calculated for the diffuse sound field Lr only. *3 “The noise level must (in accordance with DIN VDE 0833-4 VDE 0833-4:2024-06) be representative of the intended emergency scenarios, i.e., if necessary, additions or deductions must be applied to the determined noise levels. These additions or deductions to the noise level can be taken into account in the PAUL 1.07 software.
Note on B12: Oktav-Störpegel Ln im Diffusfeld Lr

## 2 Background Noise (Machine)
Anzahl der Quellen (z. B. Maschinen)→ | 1 | Background Noise Level Calculation Tool, Version 1.1 Lw
Room Volume [m³] → | 1000
Octave Band values | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz
RT60 [s] → | 1 | 1 | 1 | 1 | 1 | 1 | 1
Octave Band values | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
Sound Power Levels LW [dB ] (*1) | 111.5 | 111.5 | 111.5 | 111.5 | 111.5 | 111.5 | 111.5 | 119.951 | 118.485
| 0.14125 | 0.14125 | 0.14125 | 0.14125 | 0.14125 | 0.14125 | 0.14125
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.98878
| 95.4 | 102.9 | 108.3 | 111.5 | 112.7 | 112.5 | 110.4
| 0.0034674 | 0.019498 | 0.067608 | 0.14125 | 0.18621 | 0.17783 | 0.10965 | 0.70551
Noise-Level Results Ln in dB SPL (*2) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
maschine (calculated from Lw) | 95.4523 | 95.4523 | 95.4523 | 95.4523 | 95.4523 | 95.4523 | 95.4523 | 103.9033 | 102.4374
Sum of 10*Antilog | 0.0035094 | 0.0035094 | 0.0035094 | 0.0035094 | 0.0035094 | 0.0035094 | 0.0035094
A-weighting (dB) | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.024566
Weighted bands | 79.3523 | 86.8523 | 92.2523 | 95.4523 | 96.6523 | 96.4523 | 94.3523
Sum of 10*Antilog | 8.6146e-05 | 0.00048443 | 0.0016797 | 0.0035094 | 0.0046263 | 0.0044181 | 0.0027242 | 0.017528
Remarks: | The example is 1 Watt of acoustical Power for all octave bands in a medium sized room. Is there any machninery that is producing noise during voice alarm? Are there people talking with sigificant level during voice alarm?
*1 input is Sound Power Level referenced to Lw = 0 dB for 10 -12 W *2 Output result is Sound Pressure Level referenced to L = 0 dB for 20 -6 Pa ¦ Noise-Level Results Ln in dB SPL are calculated for the diffuse sound field Lr only.

## Manual, Credits, Copyright
Background Noise Level Calculation Tool, Version 1.1
Background Noise Level Calculation Tool for rooms with with exponential reverberation
This Excel tool calculates the Sound Pressure Level (SPL) of background noise diffuse field Lr for rooms with exponential reverberation as a function of the number of people talking with a variety of speech levels or as a function of Noise Power Levels Lw (like from machinery, exhaust fans etc) in octave bands. It also indicates the A-weighted and Z-weighted Sound Pressure Levels of the diffuse sound field for all octave bands.
The basis for the calculation is that each octave band filtered impulse response for the room has an exponential form and can thus be characterised by a reverberation time. The acoustic system is also assumed to be linear and time invariant. The calulation tool should not be used as an alternative to real world measurements, if possible!
Tab „1 Background Noise by persons“ → For using the tool - enter input values in the green fields on :
Number of (active) persons: enter number of people talking normal, with raised speech level …
Room Volume [m³]: Enter the room volume in cubic meters
RT60 [s]: Enter the RT60 figures in seconds for all octave bands.
Noise-Level Results Ln in dB SPL: are the calculated Background Noise Level results for all octave bands and the A-weighted and Z-weighted results.
or
Tab „2 Background Noise by Lw (Machinery)“ → For using the tool - enter input values in the green fields:
Number of (active) machines: enter number of machines producing background noise
Room Volume [m³]: Enter the room volume in cubic meters
RT60 [s]: Enter the RT60 figures in seconds for all octave bands.
Sound Power Levels LW [dB ]: Enter the Lw figures of machinery or other sources for all octave bands.
Noise-Level Results Ln in dB SPL: are the calculated Background Noise Level results for all octave bands and the A-weighted and Z-weighted results in the diffuse sound field.
Project related remarks can be added in the remarks field.
This tool is intended to be used with ULYSSES 2.90 Software and PAUL 1.07 Simulation Software and has originally been created by:
Volker Löwer
IFBsoft GbR
Ginsheimer Str. 1
65462 Ginsheim-Gustavsburg
Germany
Website: www.ifbsoft.de
Mail: info@ifbsoft.de
Date: 2025-11-22
Copyright © for this tool belongs to IFBsoft GbR. The tool can be copied modified and used freely as long as not sold and a link to the original author www.ifbsoft.de will be retained. You may use the tool at your own risk. IFBsoft takes no responsibility for errors in the calculation or use of results. The sheet protection uses no password. The purpose of cell/sheet protection is only to prevent accidental or unintentional changes.
Full Disclaimer: This software tool is provided by the copyright holders and contributors IFBsoft “as is” and any express or implied warranties, including, but not limited to, the implied warranties of merchantability and fitness for a particular purpose are disclaimed. in no event shall the copyright owner or contributors be liable for any direct, indirect, incidental, special, exemplary, or consequential damages (including, but not limited to, procurement of substitute goods or services; loss of use, data, or profits; or business interruption) however caused and on any theory of liability, whether in contract, strict liability, or tort (including negligence or otherwise) arising in any way out of the use of this software, even if advised of the possibility of such damage.